INSPECTION AND TEST PLAN – WATER/RECYCLED WATER MAIN LAYING

ALL WORKS TO BE CARRIED OUT TO SYDNEY WATER STANDARDS

| Developer: | Water Servicing Coordinator: |  | WSC Site Representative: |
| --- | --- | --- | --- |
| $ | Constructor: |  | Constructor Site Representative: |
| Case No: | Accredited Driller: | Witness, Hold & Surveillance points added to ITP |
| Works classification: | Licensed Plumber RPZD: |  |
|  | Licensed Plumber Property Service (Main to Meter): |  |
|  | Plumbers Licence Number: |  |
| Works description: | Field Tester: |  |
|  | ITP Prepared by: Date / / | Reviewed by: Date / / | Sydney Water Representative Date / / |
| No | Construction/Inspection Activity | Inspection Procedure & Acceptance Criteria | Const-ructor | WSC** | Sydney Water* | Record | Comment |
| 1 | Pre-start/Site establish | Visual check. Checklist completed. | X | H | S | Checklist |  |
| 2 | Approved materials on Site/delivered | Visual check approved materials. Quantity and condition. Checklist completed | X | W | S | Checklist |  |
| 3 | Installation of cut-in | Visual and dimensional check to Sydney Water Standards | H | H | H | Water Main Connection Report |  |
| 4 | RPZD installation by an appropriate licensed plumber | Visual and dimensional check of backflow equipment and fittings | X | H | H | Checklist |  |
|  | DTC/Special Design | Visual and dimensional check to DTC or Engineers certification | X | W | S | Checklist/plan |  |
| 5 | Excavation and pipe laying | Visual and dimensional check to Sydney Water Standards. Checklist completed. | X | W | S | Checklist |  |
| 6 | Chambers | Visual and dimensional check to Sydney Water Standards. Checklist completed | X | H | S | Checklist |  |
| 7 | Survey of main in easement | Survey of pipe location before backfill | X | H | S |  |  |
| 9 | Surface fittings | Visual and dimension check to Sydney Water Standards. Checklist completed | X | X | S | Checklist |  |
| 12 | Pressure test when water is required prior to disinfection | Pressure test to Sydney Water Standards. Swabbing of main and pre-disinfection testing ie odour, clarity and turbidity test. | X | W | S | Test Results |  |
| 13 | Testing | Pressure test, Compaction test to Sydney Water Standards | X | W | S | Test Results |  |
| 14 | Disinfection | Disinfection to Sydney Water Standards | X | H | H | Test Results |  |
| 15 | Pre-connection inspection – Main | Visual inspection to Sydney Water Standards. Checklist completed | H | H | H | Checklist |  |
| 16 | Removal of RPZD by appropriately licensed plumber | Visual and dimensional check to Sydney Water Standards | X | H | H | Water Main Connection Report |  |
| 17 | Connection to System | Visual and dimensional check to Sydney Water Standards. | X | H | W | Water Main Connection Report |  |
| 17 | Property Water Connection (Drilling) | Visual and dimensional check to Sydney Water Standards. Checklist completed. | W | S | S | Checklist |  |
| 17 | Installation of property service (main to meter) | Visual and dimensional check to Sydney Water Standards. Checklist completed. | W | S | S | Checklist |  |
| 17 | Dual Water Flow Test property service/s (main to meter) | Flow test of drinking water system. Lock and tag meter ball valve. Flow test of recycled water system. Lock and tag meter ball valve. | X | W | H | Water Main Connection Report |  |
| 17 | Restoration and Post Connection Inspection | Visual inspection against photographs. Clearance letter from Council/property owner | X | H | H | Clearance letter |  |
| 17 | Validation | No | Amendment | Date | Reviewed | Symbol | Legend |
| I certify that the works have been constructed in accordance with Sydney Water Standards and the Inspection and Test Plan Water Servicing Coordinator Date / / |  |  |  |  | X | Inspection by |
|  |  |  |  |  | H | Mandatory Hold Point |
|  |  |  |  |  | W | Option given to inspect |
|  |  |  |  |  | S | Surveillance |

* Sydney Water reserves the right to vary these requirements at any time	** Sydney Water’s written approval MUST be obtained prior to varying these requirements

| WATER CONSTRUCTION CHECKLIST * Clause and Drawing No. refer to the # Refer to Provider Instructions Water Supply Code of Australia ** Refer to Technical Requirements & Work Instructions WSA 03-2011-3.1 for Water Service Connections (DRILLING) (Sydney Water Edition) ## Refer to Property Service (Main to meter) Installations Technical Requirements |
| --- |
| Case Number |  | Main layer Name: |  |
| Location |  | Pipe Size: |  |  |  |  |  |  |
|  |  | Line No: |  |  |  |  |  |  |
| WSC Rep |  | Chainage Laid: |  |  |  |  |  |  |
| No. | Description | Date: |  |  |  |  |  |  |
|  |  | Minimum Standard |  |  |  |  |  |  |
|  | Photographic record | # |  |  |  |  |  |  |
|  | Council fees paid | Council requirements |  |  |  |  |  |  |
|  | Property entry agreement | #, *Cl 11.4.1/11.5.4 |  |  |  |  |  |  |
|  | Current plan on site | #, WSC to confirm |  |  |  |  |  |  |
|  | Current Main laying Specifications on site | #, WSC to confirm, *Cl 11.1 |  |  |  |  |  |  |
|  | Kerb/footway to finished levels | # |  |  |  |  |  |  |
|  | Sydney Water listed constructor on site | #, WSC to confirm, *Cl 10.2 |  |  |  |  |  |  |
|  | Safe Work Plan on site & implemented | #, WSC to confirm, *Cl 11.5 |  |  |  |  |  |  |
|  | Environmental Management Plan on site & implemented | #, WSC to confirm, *Cl 11.5.5.1 |  |  |  |  |  |  |
|  | Inspection and Test Plan on site – one working copy | # |  |  |  |  |  |  |
|  | Traffic Management Plan on site & implemented | Industry practice, * Cl 11.5.4 |  |  |  |  |  |  |
|  | Job set out | #, WSC to confirm |  |  |  |  |  |  |
|  | Services Authorities contacted – 48 hours notice | Design Plan |  |  |  |  |  |  |
|  | All services located | # |  |  |  |  |  |  |
|  | All services marked | # |  |  |  |  |  |  |
|  | Approved materials on site | *Cl 12.1/12.4 |  |  |  |  |  |  |
|  | Delivery Inspection | *Cl 12.4 |  |  |  |  |  |  |
|  | Pipe type and size to current plan | Current Plan |  |  |  |  |  |  |
|  | Polyethylene sleeving & accessories | * Cl 12.1 |  |  |  |  |  |  |
|  | Marking tape | * Cl 12.1 |  |  |  |  |  |  |
|  | Bedding material | * WAT-1250-S/1251-S, * Cl 12.1 |  |  |  |  |  |  |
|  | Trench fill | * WAT-1250-S/1251-S, * Cl 12.1 |  |  |  |  |  |  |
|  | Fittings | * Cl 12.1 |  |  |  |  |  |  |
|  | Surface Fittings | * Cl 12.1 |  |  |  |  |  |  |
|  | Pre Cast chambers | * Cl 12.1 |  |  |  |  |  |  |
|  | Pipe laying accessories | * Cl 12.1 |  |  |  |  |  |  |
|  | Installation of cut-in | Relevant standards |  |  |  |  |  |  |
|  | Appropriate Fittings and ancillaries to stand on site | Relevant standards |  |  |  |  |  |  |
|  | RPZD Installation - Cut-In valve locked and tagged | Water Main Connection Report – Part 1 |  |  |  |  |  |  |
|  | Approval to install RPZD | Water Main Connection Report – Part 1 signed off |  |  |  |  |  |  |
|  | Accredited licensed plumber to install and provide RPZD test results | Sydney Water Back Flow Prevention Programme Accreditation |  |  |  |  |  |  |
|  | Back Flow prevention device, and fittings installation and location. | As per design plan and AS/NZS3500 Section 4.6 |  |  |  |  |  |  |
|  | Constructors site rep. On site |  |  |  |  |  |  |  |
|  | Pressure test results satisfactory |  |  |  |  |  |  |  |
|  | Traffic control, and other Safety procedures/plans in place to address special conditions. |  |  |  |  |  |  |  |
|  | Site specific EMP and SWP implemented on site | # WSC 5. Project Specific Quality Plan |  |  |  |  |  |  |
|  | All Fittings and ancillaries on site |  |  |  |  |  |  |  |
|  | Inspection and Test Plan up to date |  |  |  |  |  |  |  |
|  | Standards on site | AS/NZS3500 |  |  |  |  |  |  |
|  | Procedures and plans to address special conditions are in place i.e. Asset Isolation Plan | Flow Management and Isolation of Hydraulic Assets Procedure (HSP- 070) |  |  |  |  |  |  |
|  | Approved to connect for construction water (if no give details) | Water main Connection Report – Part 1(a) signed off |  |  |  |  |  |  |
|  | Cut-In valve unlocked and tag removed |  |  |  |  |  |  |  |
|  | Metered standpipe installed | Sydney Water Registered Stand Pipe |  |  |  |  |  |  |
|  | DTC/Special Design | # |  |  |  |  |  |  |
|  | Services marked | Dial Before You Dig, *Cl 11.5.1 |  |  |  |  |  |  |
|  | Services exposed with appropriate clearance | *Cl 11.5.1 |  |  |  |  |  |  |
|  | Trench width to standard | *WAT-1250-S/1251-S |  |  |  |  |  |  |
|  | Trench depth to standard | *WAT-1250-S/1251-S |  |  |  |  |  |  |
|  | Shoring (S) Benching (BN) Battering (BT) | *Cl 13.1/13.5/13.6 |  |  |  |  |  |  |
|  | Pipe joints Witness mark Deflection limits Restrained joints | * Cl 15 * Cl 15.1.4 * WAT-1250-S/1251-S * WAT-1208, * CL 15.7 |  |  |  |  |  |  |
|  | Valves, Hydrants and Surface fittings installed Shroud assembly Valve anchorage | * Cl 15.4 * WAT-1301-V * WAT-1207 |  |  |  |  |  |  |
|  | Bulkheads and Trench Stops to standard | *WAT-1209/1210, *Cl 15.6/15.9 |  |  |  |  |  |  |
|  | Thrust blocks to standard | *WAT-1205/1207/ 1252-S, *Cl 15.5 |  |  |  |  |  |  |
|  | Pipe embedment (bedding, surround & overlay) to standard | * WAT-1201/1202 |  |  |  |  |  |  |
|  | Concrete encasement to standard (CH-CH) | * Cl 16.6 |  |  |  |  |  |  |
|  | Marking tape to standard and correctly fitted | * WAT-1201, Cl 15.12 |  |  |  |  |  |  |
|  | Trench fill – App’d material only & layered | *WAT-1201/1250-S, *Cl 17.1 |  |  |  |  |  |  |
|  | Compaction to standard | *Cl 17.1.3 |  |  |  |  |  |  |
|  | Jointing to standard | *Cl 15.2.2 |  |  |  |  |  |  |
|  | Sleeving to standard | *Cl 15.11 |  |  |  |  |  |  |
|  | Barricades, fencing, trench plates in place & secured | OHS |  |  |  |  |  |  |
|  | Chambers to standard: in-situ (IS) Precast (PC) | *WAT-1308-V/1309 / 1350-S/1351-S, *Cl 15.13.1 |  |  |  |  |  |  |
|  | Survey of main in easement | Relevant standard |  |  |  |  |  |  |
|  | Valves, Hydrants & Surface fittings to standard | *WAT-1303-V/1305-V |  |  |  |  |  |  |
|  | Surface boxes and surrounds to finished levels | * WAT-1303-V/1305-V |  |  |  |  |  |  |
|  | Surface box lids hinged in direction of traffic flow | * WAT-1303-V/1305-V |  |  |  |  |  |  |
|  | Shroud pipes assembled to Standards | * WAT-1301-V |  |  |  |  |  |  |
|  | Fitting bolts protected to Standards | * WAT-1313 |  |  |  |  |  |  |
|  | Correct depth to Spindle tops | * WAT-1301-V |  |  |  |  |  |  |
|  | Correct depth to Hydrant lugs | * WAT-1301-V |  |  |  |  |  |  |
|  | Spindle retaining disc in place | * WAT-1301-V |  |  |  |  |  |  |
|  | Indicator plates in place | * WAT-1352-S/1353-S |  |  |  |  |  |  |
|  | Excavation to standard | NSW Code of Practice 2.218.1 |  |  |  |  |  |  |
|  | Approved products and materials – Correct Tapping Band Taptite Milnes Gunmetal Other | ** 5 Approved Products and Materials |  |  |  |  |  |  |
|  | Approved products and materials – Correct Plastic Bush White – Imperial Black - Metric | ** 5 Approved Products and Materials |  |  |  |  |  |  |
|  | Appropriate Tools Wad Cutter – PVC only Twist Drill – DICL/CICL only Plastic Sleeving – Blue Sleeve | ** 12.2 Install Drilling |  |  |  |  |  |  |
| 10.1 | Pressure test when water is required prior to disinfection | * Cl 19.4 |  |  |  |  |  |  |
| 11.1 | Compaction test | NATA Certified lab, *Cl 19.3 |  |  |  |  |  |  |
| 12.1 | Disinfection, sample & test | *Cl 20 |  |  |  |  |  |  |
| 13.1 | Site restored | *Cl 11.5.4.1, 11.5.5/ 23 |  |  |  |  |  |  |
| 13.2 | Pre connection inspection | # |  |  |  |  |  |  |
| 13.3 | Pre connection inspection Main | # > DN 250 (Isolation procedure as per Job Specific Letter) |  |  |  |  |  |  |
| 13.4 | Work As Constructed compiled – connection assumed | #, *Cl 24 |  |  |  |  |  |  |
| 14.1 | Removal of RPZD by appropriately licensed plumber | Water Main connection |  |  |  |  |  |  |
| 15.1 | Connection Safe Work Plan on site & implemented | #, WSC to confirm |  |  |  |  |  |  |
| 15.2 | Connection to live system – under pressure connection | *WAT-1105, Cl 22.2 |  |  |  |  |  |  |
| 15.3 | Connection to live system – existing system shut down | *Cl 22.1/22.2 |  |  |  |  |  |  |
| 15.4 | Thrust block to standard | *WAT-1105/1205 |  |  |  |  |  |  |
| 16.1 | Install Property service connection (Drilling) | ** 12.2 Install Drilling |  |  |  |  |  |  |
| 16.2 | Drilling in main correct | ** 12.2 Install Drilling |  |  |  |  |  |  |
| 16.3 | Location of drilling as per standard | ** 12.1 |  |  |  |  |  |  |
| 16.4 | Pipe Size within accreditation <200mm | ** 2. Scope of Water Service Connection (Drilling) |  |  |  |  |  |  |
| 16.5 | Pipe type within accreditation: DICL/CICL/PVC only | ** 2. Scope of Water Service Connection (Drilling) |  |  |  |  |  |  |
| 16.6 | Dual Water Flow Test property services (main to meter) | Water Main Connection Report |  |  |  |  |  |  |
| 16.7 | Fittings disinfected | *Cl SW20.1 |  |  |  |  |  |  |
| 16.8 | Property Water Connection (Drilling) Driller holding relevant accreditation on site | Listed Accredited Driller |  |  |  |  |  |  |
| 16.9 | Installation of property service (main to meter) Plumber holding relevant accreditation on site | AS/NZS3500 |  |  |  |  |  |  |
| 16.10 | Property boundaries located | ## 10. Installation of Property services: (Installers Responsibility), 10.1.16 Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.11 | Install property service (main to meter) – Drinking Water | ## 10. Installation of Property services: (Installers Responsibility) Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.12 | Install property service (main to meter) – Recycled Water | ## 10. Installation of Property services: (Installers Responsibility) Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.13 | Drinking water riser is plain copper | ## 10. Installation of Property services: (Installers Responsibility) Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.14 | Recycled water riser is coloured lilac | ## 10. Installation of Property services: (Installers Responsibility) Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.15 | Drinking water riser has correct ball valve | ## 10. Installation of Property services: (Installers Responsibility) Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.14 | Recycled water riser has correct ball valve | ## 10. Installation of Property services: (Installers Responsibility) Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.15 | Risers are a minimum 300mm apart | Meter Fit Policy |  |  |  |  |  |  |
| 16.16 | Drinking Water non-return valve fitter |  |  |  |  |  |  |  |
| 16.17 | Termination of property service as per standard | ## 10.1.2 – 10.1.3 AS/NZS3500 |  |  |  |  |  |  |
| 16.18 | Embedment and trench fill – drinking water property services | AS/NZS3500 |  |  |  |  |  |  |
| 16.19 | Embedment and trench fill – recycled water property services | AS/NZS3500 |  |  |  |  |  |  |
| 16.20 | Clearance from other services | ## 10. Installation of Property services: (Installers Responsibility), 10.1.7 Current NSW Code of Practice for Plumbing and Drainage AS/NZS3500 |  |  |  |  |  |  |
| 16.21 | Drinking water property services locked & tagged |  |  |  |  |  |  |  |
| 16.22 | Recycled water property services locked & tagged |  |  |  |  |  |  |  |
| 17.1 | Site clear & final restoration | *Cl 23 |  |  |  |  |  |  |
| 17.2 | Road/Footpath Opening | ** 6.2 Work Site Assessment |  |  |  |  |  |  |
| 17.3 | Dial Before You Dig | ** 6 Excavation, 6.1 |  |  |  |  |  |  |
| 18.1 | Safe Work Plan On Site | ** 12.1 |  |  |  |  |  |  |
| 18.2. | Safe Work Plan Implemented | ** 12.1 |  |  |  |  |  |  |
| 18.3 | Environmental Management Plan on site | ** 12.1 |  |  |  |  |  |  |
| 18.4 | Environmental Management Plan implemented/site prepared | ** 12.1 |  |  |  |  |  |  |
| 19.1 | Validation | # |  |  |  |  |  |  |
| 20.1 | Inspection & Test Plan signed off | # |  |  |  |  |  |  |
| This is to certify that excavation & installation of infrastructure has been in compliance with Sydney Water Standards and in accordance with Company OHS & Environmental Policies | Signed:………………………………………….………. Date: ……………………… (Sydney Water listed constructor responsible for construction) |