| Water assets: <250mm, or 250mm & greater already identified as W3 with low customer and system risks |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Project Title / Name: |  |  |  |  |  |  |  | MAXIMO No: |  |  |  |  |  |  |  |
| ISOLATION PLANNING |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Does the project involve confined space entry or excavation with a depth of 1.5m or greater? If No, W3, Single Barrier Routine, If Yes, W4: Double Barrier OR W5: Single Barrier with second control other than additional barrier |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Method of hydraulic flow isolation / flow management (tick relevant): |  |  |  |  |  |  |  |  | W3 ☐ W4 ☐ W5 ☐ |  |  |  |  |  |  |
| If W5, select one second control (i.e. |  | Monitor SV to prevent valve from being accidentally operated OR, |  |  |  |  |  |  | ☐ |  |  |  |  |  |  |
|  |  | Lock single valve so it cannot be operated OR, |  |  |  |  |  |  | ☐ |  |  |  |  |  |  |
|  |  | Use a barrier (e.g. plate) to stop access to single valve so it cannot be operated. |  |  |  |  |  |  | ☐ |  |  |  |  |  |  |
| Are valves to be operated and method for proving isolation identified on attached plan(s)? |  |  |  |  |  |  |  |  | Yes ☐ No ☐ |  |  |  |  |  |  |
| - Plan Approved by Responsible Manager or Delegated Rep: |  |  |  |  |  |  |  |  | Date: |  |  |  |  |  |  |
| ISOLATION IMPLEMENTATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hazard | Impact |  |  |  |  | CONTROLS |  |  | CONTROLS HAVE BEEN IMPLEMENTED |  |  |  |  |  |  |
| What can harm you? | What can it happen? |  |  | How can it happen? |  |  |  |  |  |  |  |  |  |  |  |
| Engulfment of the work site | Drowning of personnel |  |  | SVs isolating main are operated during works |  | - All isolation valves to be operated and tagged by the authorised person, as per LOTO Procedure |  |  | Yes ☐ |  |  | No ☐ |  |  |  |
| Engulfment of the work site | Drowning of personnel |  |  | Unanchored / unrestrained valves |  | - All 1st barrier SVs to be greater than 10m from work excavation or double barrier to be implemented |  |  | Yes ☐ |  |  | No ☐ |  |  |  |
| Engulfment of the work site | Drowning of personnel |  |  | Internal leaking of isolation valves |  | - FIFM completed & successfully proven via: _______________________________ (e.g. hydrant outside No. 36 Kay St) |  |  | Yes ☐ |  |  | No ☐ |  |  |  |
| Engulfment of the work site | Drowning of personnel |  |  | Entrapment in: - A confined space or - An excavation with a depth of 1.5m or greater |  | - Double barrier isolation OR - Lock single valve so it cannot be operated, as per LOTO Procedure, OR - Prevent access to the single valve by using a barrier (such as a plate) OR - Monitor SV to prevent valve from being inadvertently operated |  |  | Yes ☐ |  |  | No ☐ |  |  | N/A ☐ |
| Work can proceed only if controls for hazards identified as applicable have been implemented. If “No” has been marked for any of the above cease work and refer to Team Leader / Manager. The FIFM incorporates the relevant SWMS. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Work cannot commence until this section has been signed |  |  |  |  |  |  | Name (Print) |  | Signed |  |  |  |  | Date |  |
| - FIFM completed as per HYDRA plot & I have personally witnessed the FIFM successfully proven |  |  |  |  | Responsible Person Implementation |  |  |  |  |  |  |  |  |  |  |
| - Controls for hazards identified above as applicable have been applied |  |  |  |  | Responsible Person Implementation |  |  |  |  |  |  |  |  |  |  |
| - Work Authorised to commence |  |  |  |  | FIFM Plan Coordinator |  |  |  |  |  |  |  |  |  |  |
| - Authority to commence acknowledged |  |  |  |  | Service Provider |  |  |  |  |  |  |  |  |  |  |

| RECOMMISSIONING |  |  |  |  |
| --- | --- | --- | --- | --- |
| Criteria | Role | Name (Print) | Signed | Date |
| - Work has been completed to the stage where the asset is now available for recommissioning | Service Provider |  |  |  |
| - Asset is now available for recommissioning | FIFM Plan Coordinator or delegated rep |  |  |  |
| - Authority to recommission assets acknowledged | Responsible Person Implementation |  |  |  |
| - Recommissioning complete, system returned to normal operation, FIFM Plan Coordinator notified. | Responsible Person Implementation |  |  |  |

## Related Documents

| Parent document number | Parent document title |
| --- | --- |
| 1283296 | Flow Isolation and Flow Management (FIFM) Procedure |