SEWAGE PUMPING STATIONS DRY WELL VENTILATION design checklist

The following design checklist is a guide only, based on the Design Specification for Sewage Pumping Stations Dry Well Ventilation (D0001896). The list is not exhaustive and full responsibility for complying with relevant specifications, codes and standards lies with the designer. The checklist must be completed by the design verifiers and submitted with design drawings.

| SPS No: | Location: | Project No: |  | Delivery Contractor: |  |
| --- | --- | --- | --- | --- | --- |
| Design Stage: | Design Team: |  | Verifiers: |  | Date: |

| ITEM | REQUIREMENTS | YES | NO | N/A | CLAUSE REF. |  | DESCRIPTION |
| --- | --- | --- | --- | --- | --- | --- | --- |
| GENERAL |  |  |  |  |  |  |  |
| Ventilation System Type | Dilution ventilation system. |  |  |  | 2 |  |  |
|  | Supply ventilation system only. |  |  |  | 2 |  |  |
| Air Supply Points | To bottom 3m of the dry well. |  |  |  | 2 |  |  |
|  | To each landing. |  |  |  | 2 |  |  |
|  | To any electrical switchboard and control cubical platform below ground level. |  |  |  | 2 |  |  |
|  | Multiple supply points where 'throw' exceeds 5m. |  |  |  | 2 |  |  |
| Air Volume Design Flow Rates | - Minimum 400L/s irrespective of dry well size, OR - 20 air changes per hour to the bottom 3m of the dry well, OR - 17L/s/m2 of the plan area of the dry well, whichever is greater, PLUS - 5L/s/m2 of any landing/platform area below ground level. |  |  |  | 3 |  |  |
| Pressure maintained in dry well and superstructure | 40Pa - 50Pa above atmospheric in the dry well and superstructure when all entry doors are closed. |  |  |  | 6 |  |  |
| Noise | Internal noise level does not exceed 70dB(A) at 1m from the fan in any direction (with superstructure doors closed and pumps not operating). |  |  |  | 10 |  |  |
|  | External noise level complies with the requirements of Sydney Water Technical Specification – Mechanical. |  |  |  | 10 |  |  |
| Toilets, Amenities and Store | If separated from the dry well, provided by either natural or mechanical means to the requirements of The National Construction Code of Australia, noting the need for separation between intake and exhaust locations. |  |  |  | 11 |  |  |
| Ventilation System Failure | In the event of mechanical or electrical failure a fault signal will be sent through IICATS, and the green indication beacon turns off. |  |  |  | 12 |  |  |
|  | Ventilation System failure alarm is failsafe. |  |  |  | 12 |  |  |
| AIR DIFFUSION AND VELOCITY |  |  |  |  |  |  |  |
| Air Diffuser Positioning | Positioned so that the air flow is not inhibited by plant and equipment. |  |  |  | 4 |  |  |
|  | Air flow from the diffusers is directed to avoid dead spots within the bottom 3m of the dry well. |  |  |  | 4 |  |  |
|  | Air diffusers are reachable from the floor or intermediate landings (typically 2.3m - 2.4m to centreline). |  |  |  | 4 |  |  |
|  | Air diffusers spaced so that there are no zones of low velocity between their discharge angles. |  |  |  | 4 |  |  |
| Air Diffusers Type | Fitted with either adjustable jet or distribution type nozzles. |  |  |  | 4 |  |  |
|  | Have two-dimensional direction adjustment. |  |  |  | 4 |  |  |
| Air Velocity | Approx. 1.5m above the floor or landing AND 2.5m from the supply point the air velocity meets the following criteria: - For jet distribution diffusers, the velocity is 0.5m/s - 1.0m/s - For diffuse distribution diffusers, the velocity is 0.2m/s - 0.5m/s. Velocities are achieved within the diffuser's discharge angle. |  |  |  | 4 |  |  |
|  | Air velocity ≥0.1m/s at any point at the dry well floor. |  |  |  | 4 |  |  |
|  | Air velocity at the dry well sump is no less than 0.5m/s. |  |  |  | 4 |  |  |
| DUCTING |  |  |  |  |  |  |  |
| Duct Sizing and Selection Parameters | Ducts and louvres are sized so that velocities do not exceed the following values: - Main duct - 10m/s - Branch duct - 8m/s - Exhaust louvres - 6m/s - Intake louvres - 2m/s. |  |  |  | 5 |  |  |
|  | Flow capacity test points are provided at accessible locations positioned between 1m and 2.4m above the floor/platform level. |  |  |  | 5 |  |  |
|  | Test points are DN32 plastic electric cable glands with end plugs, preferably located not less than 5 x duct diameters from any item than can cause flow disturbance. |  |  |  | 5 |  |  |
|  | At least one test point is provided at the fan (preferably downstream) and one upstream of each diffusor. |  |  |  | 5 |  |  |
|  | Two pressure sensing nipples are provided with plastic tubing and connected to the pressure switch or pressure transmitter. |  |  |  | 5 |  |  |
|  | Volume control dampers, where installed, are located at suitable and convenient locations for commissioning. |  |  |  | 5 |  |  |
|  | Dampers are adjustable type with an operating lever and provision for its securing in the required position. Final position of the damper flap/operating lever permanently marked. |  |  |  | 5 |  |  |
|  | Ductwork and dampers are stainless steel Gr 316. |  |  |  | 5 |  |  |
|  | Flexible connectors installed at inlet and outlet of each fan, and where required in the duct runs. |  |  |  | 5 |  |  |
|  | Flexible connections made of suitable material and designed to allow 25mm movement in required directions. |  |  |  | 5 |  |  |
|  | Flexible connections suitable for outdoor service and temperature ranges from 10°C - 100°C and pressure to 35kPa. |  |  |  | 5 |  |  |
|  | Bottom of any ducts and duct supports are a min 2m above the floor or any operating landing level. |  |  |  | 5 |  |  |
|  | Louvres are vandal (no screw heads visible), rainwater, vermin, bird, and ember proof and acoustically rated. |  |  |  | 5 |  |  |
|  | Louvres are heavy duty, industrial grade with blades made of minimum 1.5mm thick and external frames from min. 3mm thick stainless steel Gr. 316 plates with matte finish to reduce reflection. |  |  |  | 5 |  |  |
|  | Ductwork complies with AS4254.1, AS4254.2 and/or SMACNA HVAC Duct Construction Standards, Metal and Flexible. |  |  |  | 5 |  |  |
| Ductwork - Painting | Ductwork, louvres, and diffusers internal to the building are unpainted unless there are specific heritage requirements. |  |  |  | 5 |  |  |
|  | Ductwork and louvres external to the building are unpainted unless there are specific heritage, environment, or community requirements. |  |  |  | 5 |  |  |
|  | Painting, where required, complies with WSA 201. The colour specified suits the local environment or to match the existing colour scheme for heritage listed sites. External components painted to PUR-B or PSL paint systems. |  |  |  | 5 |  |  |
| AIR INTAKE AND EXHAUSTS |  |  |  |  |  |  |  |
| Air Intake Location Criteria | 6m minimum from any wet well intake and exhaust vents. |  |  |  | 7 |  |  |
|  | 6m minimum from any dry well ventilation exhaust vents. |  |  |  | 7 |  |  |
|  | 6m minimum from the pump station entry doors. |  |  |  | 7 |  |  |
|  | Minimum 1m above ground level. |  |  |  | 7 |  |  |
|  | Preferably facing the direction of prevailing winds. |  |  |  | 7 |  |  |
|  | Positioned min. 500mm above the 1% AEP flood level. |  |  |  | 7 |  |  |
| Air Exhaust Points Criteria | Minimum 6m from the nearest property boundary. |  |  |  | 7 |  |  |
|  | Preferably 6m, or as far as practicable from any wet well intake and exhaust points, access openings or penetrations. |  |  |  | 7 |  |  |
|  | Preferably in the direction of prevailing winds. |  |  |  | 7 |  |  |
|  | Positioned min. 500mm above the 1% AEP flood level. |  |  |  | 7 |  |  |
| Openings, Gaps and Penetrations | All openings, vents, gaps in joints and penetrations between the dry and wet well are sealed air and watertight. |  |  |  | 7 |  |  |
|  | All other ductwork penetrations through the superstructure walls to be preferably located 500mm above 1% AEP flood level. |  |  |  | 7 |  |  |
| FANS |  |  |  |  |  |  |  |
| Fan Selection and Location | Three phase. |  |  |  | 8 |  |  |
|  | Wherever possible, in-line duct mounted axial fan. |  |  |  | 8 |  |  |
|  | Fan body material is Gr. 316 stainless steel. |  |  |  | 8 |  |  |
|  | Fan propeller material is Gr. 316 stainless steel or FRP |  |  |  | 8 |  |  |
|  | Fan mounted on adequate rubber in shear anti-vibration mounts. |  |  |  | 8 |  |  |
|  | Fans supported from a structural element such as wall or beams but not off the ductwork itself. |  |  |  | 8 |  |  |
|  | Located in an easily accessible location for maintenance. |  |  |  | 8 |  |  |
|  | Fan el. junction box face main access area and easily reachable. |  |  |  | 8 |  |  |
|  | Fan and control panel located in the station superstructure min. 300mm above the 1% AEP flood level. |  |  |  | 8 |  |  |
|  | Selected fans and motors have the capability of increasing the 'as built' system flow rate by 10%. |  |  |  | 8 |  |  |
| Operation | Fan designed for 24-hour operation. |  |  |  | 9.1 |  |  |
|  | No stand-by capacity provided. |  |  |  | 9.1 |  |  |
|  | 415V 3-phase & earth four-pin power supply for a portable emergency fan provided. |  |  |  | 9.1 |  |  |
|  | Fans electrical panels are stand-alone panels. |  |  |  | 9.1 |  |  |
|  | Fan isolator located near the fan in an easily reachable location and approximately 1500mm above the operating platform. |  |  |  | 9.1 |  |  |
|  | Green air flow status indication light visible from the entry door. |  |  |  | 9.1 |  |  |
|  | Signage visible from the entry door indicating that when the green light is on the ventilation system is 'healthy'. |  |  |  | 9.1 |  |  |
|  | The sign is a traffolyte, colour red with white lettering "GREEN LIGHT INDICATES DRY WELL VENTILATION AIRFLOW IS HEALTHY". Lettering is minimum 20mm capital Arial font. |  |  |  | 9.1 |  |  |
|  | If more access doors (including roller doors with integral personnel door), all doors have switches to initiate high speed fan operation. |  |  |  | 9.1 |  |  |
| Fans Smaller than 0.5kW | Single speed driven with direct on-line starters. |  |  |  | 2.1 & 9.2 |  |  |
|  | Designed to run at full speed all the time delivering the design airflow and pressure. |  |  |  | 2.1 & 9.2 |  |  |
|  | Pressure sensing connections on the suction and discharge sides of the fan connected via plastic tubing to a pressure switch. |  |  |  | 9.2 |  |  |
|  | Pressure switch located close to the fan approx. 1500mm above the operating platform. |  |  |  | 9.1 & 9.2 |  |  |
|  | Green indication beacon (24V DC) illuminates to shown that the ventilation system is healthy. |  |  |  | 9.2 |  |  |
|  | IICATS alarm configured for when the duct pressure drops below the set point, or the fan is turned off. This also turns off the indication beacon. (Alarm signal sent to SOC and locally at the fan electrical panel door). |  |  |  | 9.1 & 9.2 |  |  |
| Fans 0.5kW or larger | Provided with VSD |  |  |  | 2.2 & 9.2 |  |  |
|  | Designed to run at low speed (normal operation) when the entry doors are closed, and the station is not occupied (50-60% of the design airflow) and at high speed when any of the entry doors is open (100% of the design airflow). |  |  |  | 2.2 & 9.3 |  |  |
|  | Pressure sensing connections on the suction and discharge sides of the fan connected via plastic tubing to a pressure transmitter. |  |  |  | 9.2 |  |  |
|  | Pressure transmitter to be located close to the fan approx. 1500mm above the operating platform. |  |  |  | 9.2 |  |  |
|  | Green indication beacon (24V DC) illuminates to shown that the ventilation system is healthy. |  |  |  | 9.3 |  |  |
|  | IICATS alarm is configured for when the duct pressure drops below the set point, or the fan is turned off. This will also turn off the indication beacon. (Alarm signal sent to SOC and locally at the fan electrical panel door). |  |  |  | 9.3 |  |  |
|  | Entry door switches provided to initiate high speed fan operation mode when the door is opened. |  |  |  | 9.3 |  |  |

- Ownership

- Ownership

BMIS number:	D0002343

| Role | Title |
| --- | --- |
| Group | Engineering and Technical Support |
| Owner | Manager, Engineering |
| Author | Milan Rubcic, Technical Director - Mechanical |

- Change history

| Version | Prepared by | Date | Reviewed by | Approved by | Issue date |
| --- | --- | --- | --- | --- | --- |
| 1 | Milan Rubcic | 7/5/2024 | Mark Mordini | Norbert Schaeper | 7/05/2024 |

- Revision details

| Version No. | Clause | Description of revision |
| --- | --- | --- |
| 1 | First issue | Not applicable. |